## Slide 1
PEK-130
Three-Phase Inverter

## Slide 2
PSIM Functions
Digital Control Implementation
(SimCoder + TI DSP Target)
PEK-130 Inverter Hardware Introduction
Lab 1: Three-phase SPWM
Lab 2: Three-phase Stand-alone Inverter
Lab 3: Three-phase Grid-Connected Inverter
Lab 4: Single-phase Interleaved Bridgeless PFC Rectifier
Lab 5: Single-phase Three-arm Rectifier-Inverter For UPS
Contents

## Slide 3
PSIM Functions

## Slide 4
Digital Control Implementation
(On-line tuning of control parameters)
SimCoder + TI DSP Target

## Slide 5
PSIM SimCoder
The element with CG and TI on the left column of the element can be used for code generation

## Slide 6
System in Continuous Domain
System with SimCoder for Code Generation of Hardware Target
System in Discrete Domain
Code Generation - A Step-by-Step Approach

## Slide 7
#include<math.h> #include"PS_bios.h" typedef float DefaultType; #defineGetCurTime() PS_GetSysTimer() interrupt void Task(); DefaultTypefGbliref = 0; DefaultTypefGblU2 = 0; interrupt void Task() { DefaultTypefU2, fSUMP1, fSUMP3, fk3, fk1, fSUM1, fZ1, fTI_ADC1, fVDC2; PS_EnableIntr(); fU2 = fGblU2;
fTI_ADC1 = PS_GetDcAdc(0);
fVDC2 = 2;
fZ1 = fTI_ADC1;
fSUM1 = fVDC2 - fZ1;
fk1 = fSUM1 * 0.4;
fk3 = fSUM1 * (1000.0/20000);
fSUMP3 = fk3 + fU2;
fSUMP1 = fk1 + fSUMP3;
PS_SetPwm1RateSH(fSUMP1);
#ifdef_DEBUG
fGbliref = fVDC2;
#endif
fGblU2 = fSUMP3;
PS_ExitPwm1General();
}
void Initialize(void)
{
PS_SysInit(30, 10);
PS_StartStopPwmClock(0);
PS_InitTimer(0, 0xffffffff);
PS_InitPwm(1, 0, 20000*1, (4e-6)*1e6, PWM_POSI_ONLY, 42822);// pwnNo, waveType, frequency, deadtime,
outtype
PS_SetPwmPeakOffset(1, 10, 0, 1.0/10);
PS_SetPwmIntrType(1, ePwmIntrAdc0, 1, 0);
PS_SetPwmVector(1, ePwmIntrAdc0, Task);
PS_SetPwmTzAct(1, eTZHighImpedance);
PS_SetPwm1RateSH(0);
PS_StartPwm(1);
PS_ResetAdcConvSeq();
PS_SetAdcConvSeq(eAdc0Intr, 0, 1.0);
PS_AdcInit(1, !1);
PS_StartStopPwmClock(1);
}
void main()
{
Initialize();
PS_EnableIntr(); // Enable Global interrupt INTM
PS_EnableDbgm();
for (;;) {
}
}
Code Generation
The control in this block will be transferred to be C code

## Slide 8
F28335 DSP Port Assignments (Pin 1 - 88)

## Slide 9
F28335 DSP Port Assignments (Pin 89 - 176)

## Slide 10
 | pin |  | 
+5V in | 1 | 2 | +5V in
GND | 3 | 4 | GND
GPIO-00 / EPWM | 5 | 6 | GPIO-01 / EPWM-1B / MFSR-B
GPIO-02 / EPWM | 7 | 8 | GPIO-03 / EPWM-2B / MCLKR-B
GPIO-04 / EPWM | 9 | 10 | GPIO-05 / EPWM-3B / MFSR-A / ECAP-1
GPIO-06 / EPWM / SYNCI / SYNCO | 11 | 12 | GPIO-07 / EPWM-4B / MCLKR-A / ECAP-2
GPIO-08 / EPWM / CANTX-B / ADCSOC-A | 13 | 14 | GPIO-09 / EPWM-5B / SCITX-B / ECAP-3
GPIO-10 / EPWM / CANRX-B / ADCSOC-B | 15 | 16 | GPIO-11 / EPWM-6B / SCIRX-B / ECAP-4
GPIO-48 / ECAP5 / XD31 (EMIF) | 17 | 18 | GPIO-49 / ECAP6 / XD30 (EMIF)
GPIO-84 | 19 | 20 | GPIO-85
GPIO-12 / TZ1n / CANTX-B / MDX-B | 21 | 22 | GPIO-13 / TZ2n / CANRX-B / MDR-B
GPIO-15 / TZ4n / SCIRX-B / MFSX-B | 23 | 24 | GPIO-14 / TZ3n / SCITX-B / MCKX-B
GPIO-24 / ECAP1 / EQEPA-2 / MDX-B | 25 | 26 | GPIO-25 / ECAP2 / EQEPB-2 / MDR-B
GPIO-26 / ECAP3 / EQEPI-2 / MCLKX-B | 27 | 28 | GPIO-27 / ECAP4 / EQEPS-2 / MFSX-B
GPIO-16 / SPISIMO-A / CANTX-B / TZ-5 | 29 | 30 | GPIO-17 / SPISOMI-A / CANRX-B / TZ-6
GPIO-18 / SPICLK-A / SCITX-B | 31 | 32 | GPIO-19 / SPISTE-A / SCIRX-B
GPIO-20 / EQEP / MDX-A / CANTX-B | 33 | 34 | GPIO-21 / EQEP1B / MDR-A / CANRX-B
GPIO-22 / EQEP1S / MCLKX-A / SCITX-B | 35 | 36 | GPIO-23 / EQEP1I / MFSX-A / SCIRX-B
GPIO-28 / SCIRX-A / -- / TZ5 | 37 | 38 | GPIO-29 / SCITX-A / -- / TZ6
GPIO-30 / CANRX-A | 39 | 40 | GPIO-31 / CANTX-A
GPIO-32 / I2CSDA / SYNCI / ADCSOCA | 41 | 42 | GPIO-33 / I2CSCL / SYNCO / ADCSOCB
ADCIN-B7 | 43 | 44 | ADCIN-A7
ADCIN-B6 | 45 | 46 | ADCIN-A6
ADCIN-B5 | 47 | 48 | ADCIN-A5
ADCIN-B4 | 49 | 50 | ADCIN-A4
ADCIN-B3 | 51 | 52 | ADCIN-A3
ADCIN-B2 | 53 | 54 | ADCIN-A2
ADCIN-B1 | 55 | 56 | ADCIN-A1
ADCIN-B0 | 57 | 58 | ADCIN-A0
GND | 59 | 60 | GND
RS232
JTAG
I/O Interface
DSP Control Board I/O Interface

## Slide 11
SimCoder Elements for TI F2833X Hardware Target
PWM generators: 3-phase, 2-phase, 1-phase, and APWM
Variable frequency PWM
Start/Stop functions for PWM generators
Trip-zone and trip-zone state
A/D converter
Digital input and output
SCI configuration, input, and output
SPI configuration, device, input, and output
CAN configuration, input, and output
Capture and capture state
Encoder and encoder state
Up/Down counter
Interrupt time
DSP clock
Hardware configuration

## Slide 12
SimCoder Elements for TI F28335 Target
PWM

## Slide 13
A/D Converter
Digital I/O
SCI
SPI

## Slide 14
Capture
Encoder
DSP Configuration
PSIM Simulation Control

## Slide 15
Experimental System
PEK-130
PTS-1000

## Slide 16
PEK-130 Main Harware Circuit

## Slide 17
F28335控制板電路圖
由雙輸出穩壓IC (TPS767-D301)提供3.3V與1.8V
信號經過二極體箝位電路以確保進入IC之電壓都在0~3V之間避免損壞DSP
透過隔離的RS232通信介面,在實驗中可即時將DSP內部信號傳回PSIM中的示波器觀測。
ADM3251(Isolated, Single-Channel
RS-232 Line Driver/Receiver)
TPS767D301
F28335

## Slide 18
I/O Configuration of PEK-130
330uF
DC
Voltage
+
-
VDC+
VDC-
10uF
Gate Drive
PWM1A
(GPIO0)
PWM1B
(GPIO1)
PWM2A
(GPIO2)
PWM2B
(GPIO3)
Start/Stop
PWM
GPIO49
Vdc
+
Vdc
-
Ks=1/3.373
Kv=1/100
Push
bottom
1mH
1mH
Kv=1/50
ADC-A0(AC)
Voab
ADC-
B0(AC)
ADC-
B6(DC)
Q1
Q2
Q3
Q4
CPLD
F28335
DSP
Protection
Circuit
RS232
SCIC
(GPIO 62, 63)
Q5
PWM3A
(GPIO4)
PWM3B
(GPIO5)
Q6
Vsa
Vsb
AC
Voltage
Vsc
1mH
10uF
10uF
Ioa
Iob
Ioc
Voab
ADC-
B1(AC)
Voab
ADC-
B2(AC)
GPIO48
ON/OFF
Voab
ADC-
B3(AC)
Voab
ADC-
B4(AC)
Voab
ADC-
B5(AC)
Vob
Voa
Load
Voltage
Voc
ILa
ILb
ILc
Isa
Isb
Isc
Kv=1/100
Ks=1/3.375
ADC-A1(AC)
ADC-A2(AC)
ADC-A5(AC)
ADC-A4(AC)
ADC-A3(AC)

## Slide 19
PEK-130 Circuit Layout
Relay
AC
Capacitor
Inductor
MOSFET
DC
Capacitor
F28335 DSP
Control Board
Gate Drive
Circuit
Test Points
RS232
JTAG
Control circuits
Hall
Current Sensor
ON/OFF
Push Bottom

## Slide 20
AC
Voltage
Load Voltage
DC
Voltage
Auxiliary Power Supply
Input
Connections

## Slide 21
Test Points
Q1, Q2, Q3, Q4, Q5, Q6: PWM signal
Ioa, Iob, Ioc, ILa, ILb, ILc: sensor factor = 1/3.375
Vsab, Vsbc, Vsca, Voab, Vobc, Voca : sensing factor = 1/100
Vdc: sensing factor = 1/50

## Slide 22
22
DSP Control Board (with Isolated RS232 port)
Flyback Auxiliary Power Supply
JTAG Module
Auxiliary Circuits
Switch Drive Power and Drive Circuit

## Slide 23
23
Gate Drive Power Circuit
Gate Drive Circuit
12V Input(Isolated)
GND
VIN+(PWM_outA)
VIN-(PWM_outB)
VIN+(+12V)
VIN- (-12V)
Photo couple MOSFET Driver
From PWM
(CPLD)
UC3845
DRV8800
VIN+(PWM_outA)
VIN-(PWM_outB)
50kHz
Gate Drive
Voltage
ON: +12V
OFF: -3.3V
12Vdc
UC3845 is used to generate
50KHz CLK signal for DRV8800

## Slide 24
DRV8800 IC
To Generate 12V square wave voltage for gate drive power
It can provide 2.8A output current
+12V
To Gate Drive Circuit
VIN+(PWM_outA)
VIN-(PWM_outB)

## Slide 25
USB_JTAG電路
ISO7240
ISO7242

## Slide 26
Auxiliary Power Supply (Flyback with multiple outputs and linear regulators)
+15V
-15V
+5V
GND
AC Input
90Vac~264Vac
+12V(Isolated)

## Slide 27
AC Current Sense Circuit

## Slide 28
AC Voltage Sense Circuit

## Slide 29
DC Voltage Sense Circuit

## Slide 30
Relay
Control Circuit
MOSFET Temperature Sense Circuit

## Slide 31
DSP Interface Circuit
3.3V5V Voltage Transform and Hardware Protection
CPLD

## Slide 32
A0 | A-phase inductor current(Io_a) | AC mode
A1 | B-phase inductor current(Io_b) | AC mode
A2 | C-phase inductor current(Io_c) | AC mode
A3 | C-phase load current(IL_c) | AC mode
A4 | B-phase load current(IL_b) | AC mode
A5 | A-phase load current(IL_a) | AC mode
A6 | X | X
A7 | X | X
B0 | AB-Line load voltage(Vo_ab) | AC mode
B1 | BC-Line load voltage(Vo_bc) | AC mode
B2 | CA-Line load voltage(Vo_ca) | AC mode
B3 | AB-Line grid voltage(Vs_ab) | AC mode
B4 | BC-Line grid voltage(Vs_bc) | AC mode
B5 | CA-Line grid voltage(Vs_ca) | AC mode
B6 | DC bus voltage(Vdc) | DC mode
B7 | X | X
AD Converter Signal Setting

## Slide 33
SimCoder AD Converter Setting

## Slide 34
SimCoder DSP Hardware Configuration(1/2)

## Slide 35
SimCoder DSP Hardware Configuration(2/2)

## Slide 36
Lab 1
Three-phase SPWM

## Slide 37
Three-phase Sinusoidal PWM (SPWM)

## Slide 38
Three-phase SPWM Output Voltage

## Slide 39
Space Vector PWM (SVPWM)

## Slide 40
SVPWM Voltage Vector

## Slide 41
Axis-Transformation (abc=> ab)

## Slide 42
Voltage Vector of the Space Voltage PWM
Vector space can be divided into 6 sections
Vref can be constructed with the adjacent vectors located in the same section and the zero vector

## Slide 43
Conduction Time Interval of the Voltage Vector (section 1)

## Slide 44
Conduction Time Interval of the Voltage Vectors (section 2~6)

## Slide 45
Zero-Sequence Injection (ZSI) PWM
T5
T6
T1
T2
L
IoA
T3
T4
N
C
L
L
C
C
IoB
IoC
Vd
+
_
Icapa
Icapb
Icapc
n
a
b
c
o
Zero average value method of the zero-sequence injection
It is presented to improve the conventional SVPWM that is complicated in computation
ZSI
SPWM
Zero average signal

## Slide 46
Axis Transformation
dqo to abc
abc to dqo

## Slide 47
abc to αβ
αβ to abc
Clarke and Inverse Clarke Transformation

## Slide 48
dq to αβ
αβ to dq
Park and Inverse Park Transformation

## Slide 49
Inverter Parameters
DC Voltage Vd = 100V
AC Voltage VLL = 50Vrms
Fs = 18kHz, Vtri = 5Vpp (PWM)
Cd = 330uF
L = 1mH
C = 10uF
Ks = 1/3.375 (current sensing factor)
Kv = 1/100 (AC voltage sensing), Kv = 1/50 (DC voltage sensing)

## Slide 50
3P_Inverter_1
Simulation Circuit

## Slide 51
Simulation Result

## Slide 52
Control Circuit Realized with SimCoder (Using SVPWM)
Lab1_SVPWM

## Slide 53
PWM Setting
Simulation Control Setting

## Slide 54
SCI Setting

## Slide 55
Simulation Result (Control Circuit Realized with SimCoder)

## Slide 56
Simulation Result (Control Circuit Realized with SimCoder)

## Slide 57
Lab1_ZSVPWM
Control Circuit Realized with SimCoder
(Using Zero Sequence Injection PWM)

## Slide 58
Simulation Result (Using Zero Sequence Injection PWM)

## Slide 59
Simulation Result (Using Zero Sequence Injection PWM)

## Slide 60
Lab 2: Three-phase Stand-alone Inverter
T5
T6
C
T1
T2
A
L
IoA
T1~T6
T3
T4
B
N
C
ZA
ZB
ZC
L
L
C
C
IoB
IoC
ILA
ILB
ILC
Vd
+
_
Drive circuit
PWM
circuit
S1~S6
vconA
Icapa
vconB
vconC
Icapb
Icapc
abc-to-dq
transformation
Voltage
Controller
dq-to-abc
transformation
vconq vcond
vod voq
Vab Vbc Vca
Ioa Iob Ioc
kv
ks
Current
Controller
iod
ioq
n
a
b
c
Line_abc-to-dq

## Slide 61
Inverter Modelling(1/2)
PWM

## Slide 62
1
2
Inverter Modelling(2/2)

## Slide 63
Current-Loop Control Scheme
d軸
q軸
1
+
+
+
Power circuit
-
Iod
vcond
Vcd
vff1
vfb
-
+
vff2
+
+
+
-
iod
GI
LPF
HI
+
+
+
Power circuit
-
Ioq
ioq
vconq
Vcq
vff1
vfb
+
+
vff2
+
-
+
-
GI
LPF
HI

## Slide 64
d軸
q軸
2
ILd
Vod
1/ks
1
iod
Current loop
kv
+
-
+
+
ifb
Iod
iLd
+
+
-
-
+
+
vfb
Power Circuit
Gv
LPF
HV
ILq
Voq
1/ks
1
ioq
Current loop
kv
+
-
+
+
ifb
Ioq
iLq
+
+
-
-
+
+
vfb
Power Circuit
Gv
LPF
HV
Voltage-Loop Control Scheme

## Slide 65
Gm
+
x
+
-
+
Sin(wt+p/6)
Am0
Amab
Am1
RMS Controller
RMS
Gm
+
x
+
-
+
Sin(wt-p/2)
Am0
Ambc
Am2
RMS Controller
RMS
Gm
+
x
+
-
+
Sin(wt+5p/6)
Am0
Amca
Am3
RMS Controller
RMS
abc-dq
Transformation
q
Line-abc
To
Phase-abc
Transformation
RMS Voltage Control Scheme

## Slide 66
ks: Hall sensor gain (V/A)
kv: voltage sensor gain
Set uI to be 1/8~1/10 of the switching frequency
Set z = uI/3
Set p = LPF pole
uI
z
p
HI
GI
GIHI
Type 2
Current Controller Design
Set uv to be uI/4
Set z = uv/3
Set p = LPF pole
uv
z
Hv
Gv
GvHv
Voltage Controller Design
p
Type 2

## Slide 67
% Three-phase inductor current control Inverter
clear;
clc;
PI=3.1416;
Vd=100;
L=0.6e-3;
C=10e-6;
vtm=5;
kpwm=(Vd/2)/vtm;
ks= 1/3.375;
kv=1/100;
fs=18e3;
% Current Loop Design
% Gi = k1(s+z)/s
% LPF = p/s+p
ui = 2 * PI * fs/10
z = ui/3
p = 7.23e3 * 2 * PI
tui = 1/z
numHi = kpwm*ks/L;
denHi=[1 0];
Hi=tf(numHi,denHi);
Hir = freqresp(Hi, ui);
Gc = 1/abs(Hir);
numGi1= [1 z];
denGi= [1 p 0];
Gi1 = tf(numGi1, denGi);
Gi1r = freqresp(Gi1, ui);
K1r = 1 /(abs(Hir) * abs(Gi1r));
K1 = K1r/p
numGi = K1r * numGi1;
Gi = tf(numGi, denGi);
GiHi = series(Gi, Hi);
figure(1);
bode(Hi,Gi,GiHi);
grid;
% Voltage Loop Design
% Gv = k2(s+z)/s
% LPF = p/s+p
uv = ui/4;
z = uv/3
p = 7.23e3 * 2 * PI
tuv = 1/z
numHv = kv/(ks*C);
denHv=[1 0];
Hv=tf(numHv,denHv);
Hvr = freqresp(Hv, uv);
Gc = 1/abs(Hvr);
numGv1= [1 z];
denGv= [1 p 0];
Gv1 = tf(numGv1, denGv);
Gv1r = freqresp(Gv1, uv);
K2r = 1 /(abs(Hvr) * abs(Gv1r));
K2 = K2r/p
numGv = K2r * numGv1;
Gv = tf(numGv, denGv);
GvHv = series(Gv, Hv);
figure(2);
bode(Hv,Gv,GvHv);
grid;
kpwm = 10
ks = 0.2963
kv = 0.0100
ui = 1.1310e+004
z = 3.7699e+003
p = 4.5428e+004
tui = 2.6526e-004
K1 = 2.2390
uv = 2.8274e+003
z = 942.4800
p = 4.5428e+004
tuv = 0.0011
K2 = 0.7963
Matlab Inverter Parameter Design

## Slide 68
Bode Plot of Current Loop

## Slide 69
Bode Plot of Voltage Loop

## Slide 70
Simulation Circuit (unbalanced load)
Stand_alone_LL_SVPWM_1

## Slide 71
Simulation Results

## Slide 72
Simulation Results

## Slide 73
Lab2
Control Circuit Realized with SimCoder

## Slide 74
Inductor current tracking
Q-axis
D-axis
Voltage tracking
RMS of output voltage
Q-axis
D-axis
Simulation Result (Control Circuit Realized with SimCoder)

## Slide 75
Three-phase output voltage
Three-phase inductor current
Control voltage of the three-phase SVPWM
Simulation Result (Control Circuit Realized with SimCoder)

## Slide 76
RS232 on-line waveform measurement and tuning of control parameters
Waveform measure with digital scope
Experimental circuit
Experimental Verification

## Slide 77
DQ-axis current tracking
Q-axis
D-axis
RMS output voltage (20V/div)
Q-axis
D-axis
5ms/div
Measured Waveform from RS232
DQ-axis voltage tracking

## Slide 78
Three-phase output voltage
Three-phase inductor current
Control voltage of SVPWM
5ms/div
Measured Waveform from RS232

## Slide 79
Lab 3: Three-phase Grid-connected Inverter
T1~T6
Drive circuit
S1~S6
vconA
vconB
vconC
abc-to-dq
transformation
Voltage
Controller
dq-to-abc
transformation
vconq vcond
Ioa Iob Ioc
ks
Current
Controller
iod
icq
T5
T6
C
T1
T2
A
Vd
+
_
C
L
IoA
T3
T4
B
N
L
L
IoB
IoC
a
b
c
~
~
~
n
Van
Vbn
Vcn
Vd*
Vd
Vab Vbc Vca
kv
Line_abc-to-ab
PLL
Ang
Id
Va
Vb
Ang
SVPWM
Ang

## Slide 80
There is no low-frequency voltage ripple
※ Vs(p)is the phase voltage in ab-axis
Inverter
+
Vd
-
C
Pac
Pdc
Id
+
Vd
-
C
Modeling of the Voltage Control Loop
At unity power factor
The inverter model of the two-stage system (inverter usually has a front-stage MPPT DC-DC converter) can be treated as an integrator

## Slide 81
Voltage Control Loop Design
Voltage controller
The bandwidth of voltage control loop can be wide since there is no low frequency voltage ripple
+
-
e
LPF
w(rad/s)
0dB
10
20
-10
-20
30
p
z
wc
10
100
1000
40
wc為閉迴路之零交越頻率, 相當於頻寬
p

## Slide 82
% Three-phase Rectifier
clear;
clc;
PI=3.1416;
Vd=100;
VLL=50;
Vs = 50/1.732;
Vsp = 1.5 * Vs * 1.414;
L=0.6e-3;
C=660e-6;
vtm=5;
kpwm=(Vd/2)/vtm
ks= 1/3.375
kv=1/100
kdc = Vsp/Vd;
fs=18e3;
% Voltage Loop Design
% Gv = k3(s+z)/s
% LPF = p/s+p
uv = 2 * PI * 20
z = 30
p = 7.23e3 * 2 * PI
tuv = 1/z
numHdc = kv*kdc/(ks*C);
denHdc=[1 0];
Hdc=tf(numHdc,denHdc);
Hdcr = freqresp(Hdc, uv);
Gc = 1/abs(Hdcr);
numGv1= [1 z];
denGv= [1 p 0];
Gv1 = tf(numGv1, denGv);
Gv1r = freqresp(Gv1, uv);
K3r = 1 /(abs(Hdcr) * abs(Gv1r));
K3 = K3r/p
numGv = K3r * numGv1;
Gv = tf(numGv, denGv);
GvHdc = series(Gv, Hdc);
bode(Hdc,Gv,GvHdc);
grid;
ks = 0.2963
kv = 0.0100
uv = 125.6640
z = 30
p = 4.5428e+004
tuv = 0.0333
K3 = 3.9038
Matlab Parameters Design

## Slide 83
Bode Plot of Voltage Loop

## Slide 84
Simulation of Grid-connected Inverter
Grid_Connected_LL_PLL

## Slide 85
x

x
PI

0~2p
Range
Limiter
Sin()
Cos()
w1
q
wo
+
+
-Vmcos(wt)
sin(w1t)
cos(w1t)
e
Dw
+
+

0~2p
Range
Limiter
Sin()
wi
qi
sin(wt)i
+
+
Check f
in the range ?
fmin<f<fmax
Trip of Inverter
AFD
abc-ab
Vsa
Vsb
Vsc
Vmsin(wt)
PLL
Phase Lock Loop (PLL) Controller Design

## Slide 86
Control Circuit Realized with SimCoder
Lab3

## Slide 87
Simulation Result (Control Circuit Realized with SimCoder)

## Slide 88
Measured Results(Test Points) at 150W Output Power

## Slide 89
Grid Current
DQ-Axis current tracking
Measured Results(RS232) at 150W Output Power
Q-axis
D-axis

## Slide 90
Grid Voltage
PWM control voltage
Measured Results(RS232) at 150W Output Power

## Slide 91
+
Vd
-
is*
is1
Vea
Gv
Vcon1
d1
+
Vs
-
Is
Co
Kv
Kv
vd
Ks
Vt1
PWM 1
Io
KX2
Vff
Q1
Q2
SR1
A
B
N
SR2
L
Polarity switching
ABS
ABS
GCA1
C
Q3
Q4
L
PWM 2
d2
Vcon2
Vt2
ABS
ABS
GCA2
is2
Is1
Is2
Vfb1
Vfb2
vs
vd*
Ks
Phase-1
Phase-2
Sync-arm
Lab 4: Single-phase Interleaved Bridgeless PFC Rectifier

## Slide 92
Q1
Q2
SR1
SR2
Vs
Q1
Q2
SR1
SR2
+
Vs
-
+
Vd
-
L
Is
Id
P
IGBT + SiC diode
Boost Mode
The characteristics of the ultra-fast IGBTs and SiC diodes with no recovery enable the high switching frequency PFC under CCM operation
The ultra-fast IGBTs offer the high efficiency in hard switching, low Qg, low conduction loss and high switching frequency
The low Rdson MOSFET enable synchronous line rectification and boost the efficiency
Totem-Pole Bridgeless (TPBL) PFC

## Slide 93
Q1
Q2
SR1
SR2
+
Vs
-
+
Vd
-
L
Q1
Q2
SR1
SR2
+
Vs
-
+
Vd
-
L
Q1
Q2
SR1
SR2
+
Vs
-
+
Vd
-
L
Q1
Q2
SR1
SR2
+
Vs
-
+
Vd
-
L
1
2
3
4
Operation Modes
Positive cycle (Q1 ON, SR1 ON))
Positive cycle (Q1 OFF, SR1 ON)
Negative cycle (Q2 ON, SR2 ON))
Negative cycle (Q2 OFF, SR2 ON))

## Slide 94
As Vs in positive-Cycle
VBN=0
As Vs in Negative-Cycle
VBN=Vd
1
2
1
2
3
Vs in positive-cycle
Vs in negative-cycle
vtm is amplitude of vt
Q1
Q2
SR1
SR2
+
Vs
-
+
Vd
-
L
Is
A
B
N
Q1
Q2
SR1
SR2
+
Vs
-
+
Vd
-
L
Is
A
B
N
Modelling of TPBL PFC

## Slide 95
Control Block Diagram
+
Vd
-
is*
is
Vea
Gv
Vcon
d
Vs
=Vmsinwt
Is
Co
Kv
Kv
Vd*
Vdf
Ks
Vt
PWM
Io
RMS
Vffc
Q1
Q2
SR1
Vfbc
A
B
N
SR2
L
Polarity switching
vs
ABS
ABS
GCA
sinwt
KvVm
Kff
If is=is*
=
=

## Slide 96
H is plotted with
Ks and Kv are the current and voltage sensing gains
Feedforward + Feedback control is employed in the current loop
Feedforward control is used to reduce the disturbance caused by the |Vs| and Vd
Type 2 regulator is adopted as the feedback controller GI
The zero-cross over frequency is set to be 1/8 of the switching frequency
3
pwm
k
v
pwm
k
k
1
+
+
+
+
-
sL
1
s
k
-
I
s
i
s
v
con
v
ffc
v
fbc
H
is*
GCA
u
I
z
p
H
Type 2
GCA
GCAH
Current Loop Controller Design
Kff

## Slide 97
Voltage Control Loop Modeling
Small-signal model for the two-stage system
will cause 2nd order ripple of the DC bus voltage
Considering only the real power
Derivation from the control block diagram
Small signal model
=VdIo
=
Boost
PFC
Rectifier
+
V
d
-
C
o
t
I
I
m
s
w
sin
=
P
ac
P
dc
t
V
V
m
s
w
sin
=
DC
-
DC
Converter
Io
+
-
C
o
o
I
~
d
V
~

## Slide 98
DC Voltage Control Loop
Design of the DC Voltage Controller
w(rad/s)
0dB
20
40
-20
-40
60
80
ripple attenuation
Loop response
p
z
wc
Hv
125
754
30
180
GvHv
Gv
Type 2 regulator is employed as Gv
The zero-cross over frequency (wc) is designed to be far lower than the 2nd order frequency to reduce the voltage ripple in Vea for low distortion in is*
o
sC
1
+
-
*
d
v
d
v
~
d
V
~
dcf
k
v
k
v
G
v
H
o
I
~
ea
V
~

## Slide 99
Simulation of Boost Bridgeless PFC

## Slide 100
DC voltage(Vd)
Inductor current tracking (is*, is1, is2)
Input voltage and current (Vs , Is)
Vs
Is
Simulation Results

## Slide 101
Control Circuit Realized with SimCoder

## Slide 102
Inductor current tracking (is*, is1, is2)
DC voltage (Vd)
Input voltage and current (Vs , Is)
Vs
Is
Control voltage of two phase (Vcon1 , Vcon2)
Simulation Results

## Slide 103
AC Source (single and three-phase)
DC/AC Load
PEK-130
Digital meter
Experimental Verification
RS232 on-line waveform measurement and tuning of control parameters
Waveform measure with digital scope
Experimental circuit

## Slide 104
is*
is1
is2
Measured Waveforms from RS232
Current Tracking

## Slide 105
Is
Vd
Vs
Measured Waveforms from RS232

## Slide 106
Vd
Vs
Is1
Is2
Measure Waveform from Test Points

## Slide 107
Is1
Is2
Measure Waveform from Test Points
Current Interleaving

## Slide 108
~
+
-
+
-
A
B
C
L
L
L
+
-
Load
REC-arm
COM-arm
INV-arm
N
108
(i=A, B, C)
Lab 5: Single-phase Three-arm Rectifier-Inverter For UPS

## Slide 109
+
-
+
-
+
+
Power circuit
+
-
sine-wave
generator
sint
-1
vffR
Vs
+
IA
iA
iAc
im
Vs
vconA
+
-
vsc
vfbR
vdc
Control Scheme of the Rectifier Part Circuit
kvand ks are the voltage and current sensing factors, respectively
uRI is equivalent to the bandwidth od current control loop, usually it is set to be 1/10 of the switching frequency

## Slide 110
Voltage Control Loop Modeling at Unity Power Factor
Small-signal model for the two-stage system

## Slide 111
+
-
im
vdc
Im
DC Voltage Control Loop Design
Type 2 regulator is employed as Gv
The zero-cross over frequency (wc) is designed to be far lower than the 2nd order frequency to reduce the voltage ripple in Vea for low distortion in is*
w(rad/s)
0dB
20
40
-20
-40
60
80
ripple attenuation
loop response
wc
z
GvHdc
2w1

## Slide 112
+
-
+
-
+
+
Power circuit
vfI
vo*/2
Vo/2
vconC
iC
IC
iC*
GCI
IL
k2
Vo
1/ks
1
Current loop
kv
vo
+
-
+
+
ifb
IB
iL
vo*
+
-
iC*
iC
GVI
GMI
+
-
x
RMS
sinwt
vrmsc
vrms
+
+
vm
Control Loop of the Inverter Part
Current Loop
Voltage Loop
uII is equivalent to the bandwidth of the current loop, it is usually designed to be 1/8~1/10 of the switching frequency
For achieving precise voltage regulation, a RMS loop is added to generate the voltage command of voltage loop

## Slide 113
PSIM Simulation
3-arm-REC-INV-1

## Slide 114
Simulation Result

## Slide 115
Lab6
Control Circuit Realized with SimCoder

## Slide 116
Simulation Results

## Slide 117
Vs Is
Vo Io
Vs
Is
Vo
Io
Measure Waveform from Test Points (150W resistive load)

## Slide 118
Vs Is
Vo Io
Vs
Is
Vo
Io
Measure Waveform from Test Points (100W rectified load)

## Slide 119
Vs
Is
Vdc
Vdc
Io
Ioc
Vorms
Vo
Voc
Measure Waveform from RS232 (150W resistive load)

## Slide 120
Vs
Is
Vdc
Io
Ioc
Vorms
Vo
Voc
Measure Waveform from RS232 (100W rectified load)

## Slide 121
Thank you for your attention